## Wilo+MHI
Article num main | Article num reserve | Article num archive | Brand | Series | Name | Weight, kg | Rated power, kW | Rater current, A | Connection type | Suction side DN | Pressure side DN | Fluid temp min, °С | Fluid temp max, °С | Port-to-port length, mm | Mains connection | Hydraulic performance (q1 h1 q2 h2 q3 h3…) | On live | Description | Pump image | Sizes image | Electrical diagram image | Cross-sectional drawing image | Files
4024282 |  |  | Wilo | MHI | MHI 202-1/E/1-230-50-2 | 9.8 | 0.55 | 4 | 1 | 25 | 25 | -30 | 110 | 0 | 1 | 0 23.44 0.7227 22.54 1.358 21.34 1.986 19.73 2.653 17.63 3.375 14.96 4.122 11.76 4.742 8.66 5.401 4.761 5.996 0.5769 | 0
4024283 |  |  | Wilo | MHI | MHI 202-1/E/3-400-50-2 | 8.9 | 0.55 | 1.7 | 1 | 25 | 25 | -30 | 110 | 0 | 3 | 0 23.44 0.7227 22.54 1.358 21.34 1.986 19.73 2.653 17.63 3.375 14.96 4.122 11.76 4.742 8.66 5.401 4.761 5.996 0.5769 | 0
4024284 |  |  | Wilo | MHI | MHI 203-1/E/1-230-50-2 | 9.8 | 0.55 | 4 | 1 | 25 | 25 | -30 | 110 | 0 | 1 | 1 34.31 0.6457 33.07 1.472 30.55 2.192 27.5 2.928 23.68 3.604 19.64 4.257 15.24 4.896 10.4 5.534 4.985 5.999 0.6937 | 0
4024285 |  |  | Wilo | MHI | MHI 203-1/E/3-400-50-2 | 8.9 | 0.55 | 1.7 | 1 | 25 | 25 | -30 | 110 | 0 | 3 | 0 34.31 0.6457 33.07 1.472 30.55 2.192 27.5 2.928 23.68 3.604 19.64 4.257 15.24 4.896 10.4 5.534 4.985 5.999 0.6937 | 0
4024286 |  |  | Wilo | MHI | MHI 204-1/E/1-230-50-2 | 10.6 | 0.55 | 4 | 1 | 25 | 25 | -30 | 110 | 0 | 1 | 0 44.88 0.6893 42.19 1.397 39.18 2.042 35.74 2.688 31.61 3.311 27.02 3.942 21.88 4.648 15.53 5.278 9.195 5.999 0.8094 | 0
4024287 |  |  | Wilo | MHI | MHI 204-1/E/3-400-50-2 | 9.7 | 0.55 | 1.7 | 1 | 25 | 25 | -30 | 110 | 0 | 3 | 1 44.88 0.6893 42.19 1.397 39.18 2.042 35.74 2.688 31.61 3.311 27.02 3.942 21.88 4.648 15.53 5.278 9.195 5.999 0.8094 | 0
4024288 |  |  | Wilo | MHI | MHI 205-1/E/1-230-50-2 | 12.2 | 0.75 | 5.1 | 1 | 25 | 25 | -30 | 110 | 0 | 1 | 0.5022 56.08 1.05 53.93 1.689 50.7 2.397 46.02 3.021 40.96 3.584 35.73 4.216 29.27 4.817 22.39 5.494 12.94 | 0
4210718 |  | 4148906 | Wilo | MHI | MHI 205-1/E/3-400-50-2/IE3 | 13 | 0.75 | 1.95 | 1 | 25 | 25 | -30 | 110 | 0 | 3 | 0.5022 56.08 1.05 53.93 1.689 50.7 2.397 46.02 3.021 40.96 3.584 35.73 4.216 29.27 4.817 22.39 5.494 12.94 | 0
4024290 |  |  | Wilo | MHI | MHI 206-1/E/1-230-50-2 | 15.7 | 1.1 | 7.2 | 1 | 25 | 25 | -30 | 110 | 0 | 1 | 0 69.49 0.7708 66.14 1.497 62.24 2.238 56.71 2.911 50.33 3.682 41.66 4.423 31.93 4.999 23.18 5.455 15.34 5.979 5.138 | 0
4210722 |  | 4148926 | Wilo | MHI | MHI 206-1/E/3-400-50-2/IE3 | 13.8 | 1.1 | 2.8 | 1 | 25 | 25 | -30 | 110 | 0 | 3 | 0 69.49 0.7708 66.14 1.497 62.24 2.238 56.71 2.911 50.33 3.682 41.66 4.423 31.93 4.999 23.18 5.455 15.34 5.979 5.138 | 0
|  |  | Wilo | MHI | MHI 402-1/E/1-230-50-2 | 9.8 | 0.55 | 4 | 1 | 32 | 25 | -30 | 110 | 0 | 1 | 0 22.86 1.194 22.13 2.399 20.75 3.593 18.97 4.809 16.74 5.992 13.82 6.983 10.46 7.828 6.839 8.492 3.631 | 0
4024293 |  |  | Wilo | MHI | MHI 402-1/E/3-400-50-2 | 8.9 | 0.55 | 1.7 | 1 | 32 | 25 | -30 | 110 | 0 | 3 | 0 22.86 1.194 22.13 2.399 20.75 3.593 18.97 4.809 16.74 5.992 13.82 6.983 10.46 7.828 6.839 8.492 3.631 | 0
4024294 |  |  | Wilo | MHI | MHI 403-1/E/1-230-50-2 | 10.7 | 0.55 | 4 | 1 | 32 | 25 | -30 | 110 | 0 | 1 | 0 33.52 1.205 32.3 2.376 29.92 3.683 26.71 4.798 23.11 6.026 18.28 7.208 12.4 8.075 7.364 8.988 1.671 | 0
4024295 |  |  | Wilo | MHI | MHI 403-1/E/3-400-50-2 | 9.8 | 0.55 | 1.7 | 1 | 32 | 25 | -30 | 110 | 0 | 3 | 0 33.52 1.205 32.3 2.376 29.92 3.683 26.71 4.798 23.11 6.026 18.28 7.208 12.4 8.075 7.364 8.988 1.671 | 0
4024296 |  |  | Wilo | MHI | MHI 404-1/E/1-230-50-2 | 12.2 | 0.75 | 5.1 | 1 | 32 | 25 | -30 | 110 | 0 | 1 | 0.8078 44.94 1.592 43.62 2.4 41.74 3.207 39.47 4.015 36.86 4.799 33.91 5.631 30.1 6.415 25.6 7.223 19.85 7.995 13.28 | 0
4210725 |  | 4148983 | Wilo | MHI | MHI 404-1/E/3-400-50-2/IE3 | 13 | 0.75 | 1.95 | 1 | 32 | 25 | -30 | 110 | 0 | 3 | 0.8078 44.94 1.592 43.62 2.4 41.74 3.207 39.47 4.015 36.86 4.799 33.91 5.631 30.1 6.415 25.6 7.223 19.85 7.995 13.28 | 0
4024298 |  |  | Wilo | MHI | MHI 405-1/E/1-230-50-2 | 15.2 | 1.1 | 7.2 | 1 | 32 | 25 | -30 | 110 | 0 | 1 | 0.8069 56.9 1.649 55.21 2.386 53.16 3.239 50.39 4 47.54 4.795 43.98 5.602 39.47 6.409 33.8 7.204 26.91 7.999 18.81 | 0
4210732 |  | 4149007 | Wilo | MHI | MHI 405-1/E/3-400-50-2/IE3 | 13.8 | 1.1 | 2.8 | 1 | 32 | 25 | -30 | 110 | 0 | 3 | 0.8069 56.9 1.649 55.21 2.386 53.16 3.239 50.39 4 47.54 4.795 43.98 5.602 39.47 6.409 33.8 7.204 26.91 7.999 18.81 | 0
4024300 |  |  | Wilo | MHI | MHI 406-1/E/1-230-50-2 | 17.8 | 1.5 | 9.2 | 1 | 32 | 25 | -30 | 110 | 0 | 1 | 0.8262 67.4 1.595 65.33 2.41 62.4 3.213 59.12 4.016 55.41 4.808 51.08 5.611 45.61 6.426 38.61 7.206 30.29 7.988 20.22 | 0
4210735 |  | 4149027 | Wilo | MHI | MHI 406-1/E/3-400-50-2/IE3 | 16 | 1.1 | 2.8 | 1 | 32 | 25 | -30 | 110 | 0 | 3 | 0.8262 67.4 1.595 65.33 2.41 62.4 3.213 59.12 4.016 55.41 4.808 51.08 5.611 45.61 6.426 38.61 7.206 30.29 7.988 20.22 | 0
4024302 |  |  | Wilo | MHI | MHI 802-1/E/1-230-50-2 | 15.8 | 0.75 | 5.1 | 1 | 40 | 32 | -30 | 110 | 0 | 1 | 1.429 23.58 3.036 22.76 4.484 21.92 6.052 20.8 7.52 19.48 9.028 17.76 10.5 15.64 12 12.92 13.12 10.52 13.99 8.363 | 0
4210739 |  | 4149048 | Wilo | MHI | MHI 802-1/E/3-400-50-2/IE3 | 12.3 | 0.75 | 1.95 | 1 | 40 | 32 | -30 | 110 | 0 | 3 | 1.429 23.58 3.036 22.76 4.484 21.92 6.052 20.8 7.52 19.48 9.028 17.76 10.5 15.64 12 12.92 13.12 10.52 13.99 8.363 | 0
4024304 |  |  | Wilo | MHI | MHI 803-1/E/1-230-50-2 | 14.5 | 1.1 | 7.2 | 1 | 40 | 32 | -30 | 110 | 0 | 1 | 1.413 35.38 2.517 34.81 3.505 33.94 4.531 32.89 5.48 31.76 6.525 30.32 7.493 28.77 8.519 26.88 9.526 24.79 10.75 21.98 | 0
4210743 |  | 4149067 | Wilo | MHI | MHI 803-1/E/3-400-50-2/IE3 | 13.1 | 1.1 | 2.8 | 1 | 40 | 32 | -30 | 110 | 0 | 3 | 1.413 35.38 2.517 34.81 3.505 33.94 4.531 32.89 5.48 31.76 6.525 30.32 7.493 28.77 8.519 26.88 9.526 24.79 10.75 21.98 | 0
4024306 |  |  | Wilo | MHI | MHI 804-1/E/1-230-50-2 | 16 | 1.5 | 9.2 | 1 | 40 | 32 | -30 | 110 | 0 | 1 | 1.428 47.15 2.99 45.83 4.495 43.7 6.038 40.87 7.504 37.89 9.028 34.44 10.51 30.31 12.04 24.65 13.06 19.91 13.99 15.17 | 0
4210747 |  | 4149088 | Wilo | MHI | MHI 804-1/E/3-400-50-2/IE3 | 19.1 | 1.5 | 3.7 | 1 | 40 | 32 | -30 | 110 | 0 | 3 | 1.428 47.15 2.99 45.83 4.495 43.7 6.038 40.87 7.504 37.89 9.028 34.44 10.51 30.31 12.04 24.65 13.06 19.91 13.99 15.17 | 0
4210750 |  | 4149100 | Wilo | MHI | MHI 805-1/E/3-400-50-2/IE3 | 20.5 | 2.2 | 5.4 | 1 | 40 | 32 | -30 | 110 | 0 | 3 | 1.407 59.37 2.989 57.59 4.493 55.23 5.988 52.15 7.522 48.35 9.026 43.92 10.53 38.78 12.31 31.4 13.99 22.34 | 0
4210710 |  | 4149111 | Wilo | MHI | MHI 1602-1/E/3-400-50-2/IE3 | 19 | 1.5 | 3.7 | 1 | 50 | 40 | -30 | 110 | 0 | 3 | 2.546 23.05 4.43 22.58 6.383 21.94 8.93 20.94 12 19.56 15 17.95 18 15.75 21.04 12.44 23.16 9.365 24.97 6.399 | 0
4210713 |  | 4149117 | Wilo | MHI | MHI 1603-1/E/3-400-50-2/IE3 | 21.4 | 2.2 | 5.4 | 1 | 50 | 40 | -30 | 110 | 0 | 3 | 2.539 35.14 4.937 34.31 7.547 32.97 10.09 31.39 13.05 29.4 16.05 27.05 18.97 23.81 22.01 18.68 24.93 11.92 | 0
4210715 |  | 4149123 | Wilo | MHI | MHI 1604-1/E/3-400-50-2/IE3 | 22.1 | 2.2 | 5.4 | 1 | 50 | 40 | -30 | 110 | 0 | 3 | 2.53 46.68 4.957 45.39 7.487 43.38 9.983 40.86 13 37.42 16.05 33.49 19 28.75 21.07 24.48 23.02 19.68 24.96 14.27 | 0

## Wilo+TOP-SD
Article num main | Article num reserve | Article num archive | Brand | Series | Name | Weight, kg | Rated power, kW | Rater current, A | Connection type | Suction side DN | Pressure side DN | Fluid temp min, °С | Fluid temp max, °С | Port-to-port length, mm | Mains connection | Hydraulic performance (q1 h1 q2 h2 q3 h3…) | Hydraulic performance second motor (q1 h1 q2 h2 q3 h3…) | On live | Description | Pump image | Sizes image | Electrical diagram image | Cross-sectional drawing image | Files
2044015 |  |  | Wilo | TOP-SD1 | TOP-SD 30/5 EM PN6/10 | 8.1 | 0.14 | 0.65 | 1 | 50 | 50 | -20 | 130 | 180 | 1 | 0,000 5,445 0,719 5,216 1,885 4,530 2,690 3,808 3,325 3,082 3,890 2,341 4,421 1,622 4,936 0,903 5,347 0,330 5,464 0,138 | 0,000 5,462 0,721 5,315 2,131 4,931 3,540 4,483 4,898 3,849 6,067 3,139 7,064 2,424 8,027 1,705 8,680 1,218 8,827 1,120 8,827 1,120 | 0
2044016 |  |  | Wilo | TOP-SD | TOP-SD 30/5 DM PN6/10 | 8.5 | 0.15 | 0.4 | 1 | 50 | 50 | -20 | 130 | 180 | 3 | 0,009 5,403 0,611 5,294 1,743 4,870 2,624 4,319 3,242 3,776 3,757 3,228 4,227 2,684 4,654 2,141 5,066 1,603 5,463 1,049 5,772 0,609 5,875 0,456 | 0,000 5,447 0,616 5,357 1,827 5,152 3,038 4,943 4,248 4,590 5,430 4,099 6,478 3,563 7,394 3,019 8,265 2,482 9,077 1,931 9,683 1,497 9,875 1,346 | 0
2048326 |  |  | Wilo | TOP-SD | TOP-SD 32/7 EM PN6/10 | 14 | 0.195 | 0.45 | 2 | 32 | 32 | -20 | 130 | 220 | 1 | 0,000 6,783 0,802 6,731 2,072 6,207 2,958 5,546 3,708 4,848 4,382 4,162 5,017 3,470 5,614 2,794 6,191 2,117 6,691 1,519 6,864 1,282 | 0,000 6,804 0,804 6,794 2,385 6,576 3,967 6,191 5,548 5,625 6,994 4,957 8,248 4,286 9,386 3,616 10,427 2,955 11,430 2,278 12,375 1,592 12,876 1,205 | 0
2048327 |  |  | Wilo | TOP-SD | TOP-SD 32/7 DM PN6/10 | 14 | 0.195 | 0.45 | 2 | 32 | 32 | -20 | 130 | 220 | 3 | 0,000 6,783 0,826 6,631 2,214 6,068 3,205 5,374 3,978 4,688 4,651 4,003 5,266 3,332 5,860 2,666 6,455 1,962 6,891 1,454 6,997 1,321 | 0,000 6,755 0,827 6,754 2,453 6,510 4,078 6,123 5,704 5,559 7,211 4,896 8,520 4,229 9,729 3,557 10,860 2,870 11,871 2,180 12,783 1,505 13,259 1,128 | 0
2080073 |  |  | Wilo | TOP-SD | TOP-SD 32/10 EM PN6/10 | 19.2 | 0.39 | 1.9 | 2 | 32 | 32 | -20 | 130 | 220 | 1 | 0,000 11,157 1,176 11,000 3,010 10,142 4,280 9,107 5,408 7,983 6,396 6,860 7,298 5,733 8,173 4,576 8,991 3,419 9,725 2,247 10,345 1,150 10,606 0,681 | 0,000 11,157 1,175 11,164 3,486 10,860 5,797 10,285 8,107 9,368 10,221 8,254 12,025 7,124 13,659 6,023 15,209 4,884 16,675 3,766 18,084 2,641 18,845 2,025 | 0
2165551 |  | 2080074 | Wilo | TOP-SD | TOP-SD 32/10 DM PN6/10 | 19.2 | 0.38 | 0.78 | 2 | 32 | 32 | -20 | 130 | 220 | 3 | 0,000 9,883 1,128 9,635 2,996 8,641 4,349 7,642 5,431 6,629 6,351 5,642 7,190 4,657 7,975 3,657 8,733 2,676 9,464 1,677 10,059 0,871 10,272 0,575 | 0,000 9,897 1,129 9,891 3,348 9,600 5,568 9,098 7,788 8,298 9,818 7,368 11,578 6,386 13,175 5,403 14,610 4,430 15,991 3,436 17,344 2,418 18,075 1,864 | 0
2044017 |  |  | Wilo | TOP-SD | TOP-SD 40/3 EM PN6/10 | 14 | 0.18 | 0.85 | 2 | 40 | 40 | -20 | 130 | 250 | 1 | 0,000 3,750 1,033 3,722 2,916 3,479 4,328 3,104 5,344 2,735 6,235 2,359 7,053 1,985 7,796 1,607 8,465 1,240 9,084 0,858 9,530 0,554 9,642 0,467 | 0,000 3,750 1,031 3,729 3,059 3,647 5,087 3,527 7,116 3,338 9,144 3,072 11,122 2,743 12,903 2,362 14,412 1,987 15,723 1,603 16,465 1,371 16,570 1,326 | 0
2044018 |  |  | Wilo | TOP-SD | TOP-SD 40/3 DM PN6/10 | 14.4 | 0.16 | 0.4 | 2 | 40 | 40 | -20 | 130 | 250 | 3 | 0,000 3,665 1,018 3,536 2,848 3,242 4,313 2,906 5,436 2,538 6,315 2,172 7,071 1,812 7,779 1,436 8,438 1,061 9,073 0,697 9,439 0,478 | 0,000 3,651 1,016 3,597 3,014 3,492 5,012 3,380 7,010 3,213 9,009 2,975 10,958 2,654 12,688 2,287 14,150 1,914 15,490 1,549 16,246 1,337 | 0
2080075 |  |  | Wilo | TOP-SD | TOP-SD 40/7 EM PN6/10 | 21.2 | 0.39 | 1.93 | 2 | 40 | 40 | -20 | 130 | 250 | 1 | 0,000 7,192 1,783 7,084 5,078 6,630 7,602 5,908 9,356 5,190 10,810 4,479 12,136 3,746 13,377 3,028 14,532 2,316 15,559 1,661 15,979 1,397 | 0,000 7,192 1,787 7,126 5,301 6,964 8,815 6,730 12,329 6,313 15,843 5,682 19,014 4,957 21,628 4,238 23,899 3,527 25,913 2,808 27,670 2,064 28,613 1,633 | 0
2165552 |  | 2080076 | Wilo | TOP-SD | TOP-SD 40/7 DM PN6/10 | 21.2 | 0.37 | 0.76 | 2 | 40 | 40 | -20 | 130 | 250 | 3 | 0,000 6,966 1,821 6,874 5,097 6,381 7,587 5,674 9,422 4,973 10,994 4,274 12,436 3,558 13,746 2,850 14,925 2,151 15,974 1,485 16,421 1,211 | 0,000 6,995 1,824 6,933 5,412 6,736 9,001 6,470 12,589 6,036 16,089 5,426 19,152 4,739 21,778 4,041 24,141 3,324 26,285 2,623 28,298 1,905 29,304 1,560 | 0
2165553 |  | 2080077 | Wilo | TOP-SD | TOP-SD 40/10 EM PN6/10 | 29 | 0.68 | 3.47 | 2 | 40 | 40 | -20 | 130 | 250 | 1 | 0,000 10,134 2,263 9,887 6,496 9,153 9,861 8,165 12,249 7,144 14,203 6,128 15,940 5,119 17,568 4,102 19,142 3,077 20,716 2,038 21,910 1,275 22,234 1,057 | 0,000 10,104 2,198 10,050 6,521 9,748 10,843 9,382 15,166 8,837 19,489 8,057 23,495 7,087 26,922 6,083 29,927 5,062 32,616 4,051 34,619 3,262 35,253 2,996 | 0
2165554 |  | 2080078 | Wilo | TOP-SD | TOP-SD 40/10 DM PN6/10 | 29 | 0.585 | 1.17 | 2 | 40 | 40 | -20 | 130 | 250 | 3 | 0,000 9,801 2,149 9,426 6,015 8,601 9,160 7,700 11,583 6,713 13,438 5,745 15,036 4,750 16,480 3,773 17,768 2,815 18,851 1,977 19,255 1,676 | 0,000 9,829 2,151 9,612 6,383 9,130 10,614 8,667 14,845 8,113 19,077 7,363 22,999 6,448 26,353 5,481 29,294 4,495 31,926 3,514 33,887 2,738 34,570 2,450 | 0
2165555 |  | 2080079 | Wilo | TOP-SD | TOP-SD 40/15 EM PN6/10 | 38.9 | 0.945 | 4.57 | 2 | 40 | 40 | -20 | 130 | 250 | 1 | 0,000 14,980 2,020 15,031 5,603 14,131 8,421 12,565 10,618 11,017 12,481 9,530 14,105 8,022 15,586 6,539 16,971 5,077 18,356 3,558 19,407 2,492 19,655 2,258 | 0,000 15,043 1,997 15,086 5,926 14,849 9,854 14,370 13,783 13,538 17,711 12,325 21,448 10,855 24,754 9,354 27,820 7,874 30,742 6,347 32,037 5,652 | 0
2165556 |  | 2080080 | Wilo | TOP-SD | TOP-SD 40/15 DM PN6/10 | 39.8 | 0.905 | 1.84 | 2 | 40 | 40 | -20 | 130 | 250 | 3 | 0,000 15,551 0,594 15,596 2,055 15,597 5,899 14,686 8,954 13,105 11,172 11,516 12,996 10,009 14,622 8,436 16,150 6,891 17,579 5,369 18,959 3,797 19,945 2,632 20,190 2,337 | 0,002 15,484 1,997 15,563 6,040 15,258 10,083 14,871 14,127 14,160 18,173 13,018 21,925 11,588 25,282 10,058 28,393 8,520 31,208 6,953 32,789 6,031 32,998 5,901 | 0
2165557 |  | 2080081 | Wilo | TOP-SD | TOP-SD 50/7 EM PN6/10 | 31 | 0.69 | 3.49 | 2 | 50 | 50 | -20 | 130 | 280 | 1 | 0,000 7,421 2,752 7,399 8,166 6,952 12,853 6,243 16,220 5,503 18,729 4,754 20,775 4,022 22,558 3,281 24,208 2,518 25,726 1,780 26,717 1,264 26,966 1,137 | 0,000 7,419 2,750 7,401 8,158 7,318 13,566 7,118 18,975 6,699 24,383 6,155 29,791 5,547 34,870 4,858 39,091 4,128 42,455 3,390 44,104 2,985 | 0
2165558 |  | 2080082 | Wilo | TOP-SD | TOP-SD 50/7 DM PN6/10 | 31 | 0.61 | 1.19 | 2 | 50 | 50 | -20 | 130 | 280 | 3 | 0,000 7,331 2,832 7,230 8,401 6,683 13,156 5,985 16,552 5,245 19,133 4,491 21,239 3,754 23,073 3,031 24,839 2,288 26,605 1,539 28,031 0,972 28,481 0,786 | 0,000 7,360 2,829 7,305 8,394 7,125 13,959 6,887 19,524 6,468 25,089 5,880 30,518 5,176 35,405 4,439 39,341 3,694 42,395 2,942 44,634 2,272 45,383 2,027 | 0
2165559 |  | 2080083 | Wilo | TOP-SD | TOP-SD 50/10 EM PN6/10 | 33.5 | 0.82 | 3.94 | 2 | 50 | 50 | -20 | 130 | 280 | 1 | 0,000 9,059 3,162 9,025 9,305 8,582 13,932 7,609 16,814 6,680 19,241 5,759 21,440 4,857 23,488 3,964 25,384 3,072 27,128 2,167 28,721 1,219 29,555 0,735 | 0,000 9,020 3,161 9,032 9,379 8,916 15,596 8,718 21,814 8,252 27,728 7,480 32,809 6,573 36,979 5,652 40,694 4,748 44,182 3,819 47,443 2,910 49,945 2,232 50,706 2,019 | 0
2165560 |  | 2080084 | Wilo | TOP-SD | TOP-SD 50/10 DM PN6/10 | 33.5 | 0.88 | 1.73 | 2 | 50 | 50 | -20 | 130 | 280 | 3 | 0,000 9,583 2,097 9,498 7,476 9,194 12,651 8,364 16,326 7,371 19,250 6,399 21,800 5,436 24,200 4,494 26,450 3,510 27,875 2,866 28,193 2,750 | 0,000 9,637 3,125 9,599 9,271 9,352 15,417 9,077 21,563 8,622 27,710 7,919 33,556 6,997 38,578 6,027 42,775 5,077 46,448 4,115 49,221 3,311 50,123 3,017 | 0
2165561 |  | 2080086 | Wilo | TOP-SD | TOP-SD 50/15 DM PN6/10 | 46.5 | 1.57 | 3.13 | 2 | 50 | 50 | -20 | 130 | 340 | 3 | 0,000 15,944 3,942 15,776 10,938 14,602 16,611 13,097 21,150 11,528 24,932 9,950 28,336 8,308 31,361 6,662 34,103 5,081 36,751 3,460 39,020 2,109 39,759 1,622 | 0,000 15,992 3,953 16,012 11,727 15,554 19,501 14,814 27,275 13,777 35,050 12,371 42,160 10,773 48,133 9,156 53,443 7,526 58,278 5,904 62,070 4,523 63,515 4,038 | 0
2165562 |  | 2080087 | Wilo | TOP-SD | TOP-SD 65/10 EM PN6/10 | 38.5 | 0.79 | 3.78 | 2 | 65 | 65 | -20 | 130 | 340 | 1 | 0,000 8,247 4,240 8,068 11,156 7,129 16,343 6,313 21,022 5,487 25,090 4,670 28,548 3,840 31,600 3,015 34,448 2,178 37,295 1,332 39,126 0,773 39,461 0,669 | 0,000 8,304 4,242 8,313 12,585 7,970 20,928 7,416 29,271 6,770 37,614 6,043 45,550 5,249 52,570 4,419 58,675 3,581 63,864 2,738 67,221 2,142 68,039 2,004 | 0
2165563 |  | 2080088 | Wilo | TOP-SD | TOP-SD 65/10 DM PN6/10 | 38.5 | 0.845 | 1.67 | 2 | 65 | 65 | -20 | 130 | 340 | 3 | 0,000 8,600 4,361 8,289 11,789 7,395 17,543 6,553 22,250 5,700 26,121 4,845 29,364 3,980 32,189 3,134 34,909 2,262 37,629 1,377 39,512 0,787 39,958 0,650 | 0,000 8,600 4,369 8,574 12,961 8,192 21,554 7,700 30,147 7,082 38,740 6,348 46,914 5,517 53,934 4,665 59,908 3,788 65,147 2,919 68,919 2,229 70,076 2,000 | 0
2165564 |  | 2080089 | Wilo | TOP-SD | TOP-SD 65/13 DM PN6/10 | 51 | 1.45 | 2.93 | 2 | 65 | 65 | -20 | 130 | 340 | 3 | 0,000 13,016 5,211 12,466 14,960 11,264 22,835 9,957 28,459 8,619 32,834 7,307 36,584 5,974 40,083 4,646 43,208 3,423 44,428 2,914 | 0,000 12,978 5,225 12,842 15,502 12,308 25,778 11,658 36,055 10,838 46,332 9,781 55,857 8,501 63,752 7,214 70,520 5,923 76,661 4,641 81,799 3,453 83,809 2,951 | 0
2165565 |  | 2080090 | Wilo | TOP-SD | TOP-SD 65/15 DM PN6/10 | 55.5 | 1.685 | 3.41 | 2 | 65 | 65 | -20 | 130 | 340 | 3 | 0,000 14,496 5,931 13,922 15,891 12,804 23,147 11,432 28,553 9,957 32,821 8,544 36,805 7,080 40,504 5,579 43,919 4,132 47,333 2,603 50,464 1,166 51,771 0,630 | 0,000 14,454 5,935 14,148 17,608 13,551 29,281 12,898 40,955 11,956 51,916 10,614 61,027 9,197 68,714 7,763 75,690 6,298 82,238 4,847 88,786 3,387 93,769 2,330 95,369 2,017 | 0
2165566 |  | 2080091 | Wilo | TOP-SD | TOP-SD 80/7 EM PN6 | 45.5 | 0.8 | 3.85 | 2 | 80 | 80 | -20 | 130 | 360 | 1 | 0,000 6,746 5,058 6,482 14,644 5,810 22,531 5,148 28,234 4,469 32,602 3,783 36,242 3,103 39,518 2,435 42,551 1,747 45,585 1,067 47,283 0,710 | 0,000 6,745 5,065 6,719 15,027 6,357 24,989 6,021 34,951 5,650 44,913 5,212 54,511 4,629 62,894 3,957 69,818 3,286 75,893 2,612 80,145 2,128 81,243 1,993 | 0
2165567 |  | 2080092 | Wilo | TOP-SD | TOP-SD 80/10 DM PN6 | 57.1 | 1.59 | 3.13 | 2 | 80 | 80 | -20 | 130 | 360 | 3 | 0,000 8,982 4,730 8,591 12,108 8,094 18,950 7,724 29,627 6,949 37,792 6,033 43,759 5,115 48,469 4,223 52,865 3,321 57,105 2,421 61,501 1,504 64,014 1,013 | 0,000 9,033 6,539 8,867 19,402 8,372 32,265 7,888 45,127 7,438 57,990 6,894 70,853 6,145 81,990 5,226 90,931 4,307 99,088 3,382 104,107 2,793 105,086 2,689 | 0
2165568 |  | 2080093 | Wilo | TOP-SD | TOP-SD 80/10 DM PN10 | 57.1 | 1.59 | 3.13 | 2 | 80 | 80 | -20 | 130 | 360 | 3 | 0,000 8,982 4,730 8,591 12,108 8,094 18,950 7,724 29,627 6,949 37,792 6,033 43,759 5,115 48,469 4,223 52,865 3,321 57,105 2,421 61,501 1,504 64,014 1,013 | 0,000 9,033 6,539 8,867 19,402 8,372 32,265 7,888 45,127 7,438 57,990 6,894 70,853 6,145 81,990 5,226 90,931 4,307 99,088 3,382 104,107 2,793 105,086 2,689 | 0
2165569 |  | 2080094 | Wilo | TOP-SD | TOP-SD 80/15 DM PN6 | 82.7 | 2.4 | 4.85 | 2 | 80 | 80 | -20 | 110 | 360 | 3 | 0,000 15,123 7,498 14,569 21,528 13,601 32,319 12,167 39,514 10,599 45,090 9,093 50,126 7,576 54,802 6,090 59,119 4,583 63,436 3,061 67,033 1,759 68,266 1,359 | 0,000 15,123 7,484 14,904 22,205 14,425 36,926 13,978 51,646 13,332 66,367 12,276 79,472 10,878 90,064 9,359 99,219 7,859 107,657 6,308 115,915 4,770 120,223 4,029 | 0
2165570 |  | 2080095 | Wilo | TOP-SD | TOP-SD 80/15 DM PN10 | 82.7 | 2.4 | 4.85 | 2 | 80 | 80 | -20 | 110 | 360 | 3 | 0,000 15,123 7,498 14,569 21,528 13,601 32,319 12,167 39,514 10,599 45,090 9,093 50,126 7,576 54,802 6,090 59,119 4,583 63,436 3,061 67,033 1,759 68,266 1,359 | 0,000 15,123 7,484 14,904 22,205 14,425 36,926 13,978 51,646 13,332 66,367 12,276 79,472 10,878 90,064 9,359 99,219 7,859 107,657 6,308 115,915 4,770 120,223 4,029 | 0
2165571 |  | 2080096 | Wilo | TOP-SD | TOP-SD 80/20 DM PN6 | 88.7 | 3.12 | 6.1 | 2 | 80 | 80 | -20 | 110 | 360 | 3 | 0,000 18,595 6,687 18,000 13,373 17,622 23,722 16,794 35,415 14,909 43,145 13,003 49,289 11,165 54,640 9,340 59,793 7,463 64,748 5,536 69,307 3,561 72,874 2,045 74,269 1,568 | 0,000 18,595 8,266 18,393 24,525 17,856 40,784 17,284 57,043 16,439 73,302 15,037 88,173 13,210 100,268 11,300 110,380 9,441 119,699 7,597 128,621 5,828 132,833 5,027 | 0
2165572 |  | 2080097 | Wilo | TOP-SD | TOP-SD 80/20 DM PN10 | 88.7 | 3.12 | 6.1 | 2 | 80 | 80 | -20 | 110 | 360 | 3 | 0,000 18,595 6,687 18,000 13,373 17,622 23,722 16,794 35,415 14,909 43,145 13,003 49,289 11,165 54,640 9,340 59,793 7,463 64,748 5,536 69,307 3,561 72,874 2,045 74,269 1,568 | 0,000 18,595 8,266 18,393 24,525 17,856 40,784 17,284 57,043 16,439 73,302 15,037 88,173 13,210 100,268 11,300 110,380 9,441 119,699 7,597 128,621 5,828 132,833 5,027 | 0